## Slide 1: Egress Elements
Explain how the Fire Safety Concept Tree applies to the course
Explain the purpose of the means of egress
Distinguish between the three elements of the means of egress

## Slide 2: Historic Fire
Happy Land Social Club

## Slide 3: Fire Safety Concepts Tree
Fire Safety Objectives
Prevent Fire Ignition
Manage Fire Impact
Manage Exposed
Manage Fire
NFPA 550

## Slide 4: Fire Safety Concepts Tree
Manage Exposed
Limit Amount Exposed
Safeguard Exposed
Defend Exposed in Place
Move Exposed
Cause Movement of Exposed
Provide Movement Means
Provide Safe Destination

## Slide 5: Codes
Minimum requirements
  Can exceed
Not a limit on what can be done
Based on consensus
  Best practices

## Slide 6: Egress Elements
Exit
  Meaning
  Examples

## Slide 7: Egress Elements
Exit Access
  The portion of a means of egress that leads to an exit.
Exit
  The portion of a means of egress that is separated from all other spaces of the building or structure by construction, location, or equipment as required to provide a protected way of travel to the exit discharge.
Exit Discharge
  The portion of a means of egress between the termination of an exit and a public way.

## Slide 8: Egress Elements
Public Way
  A street, alley, or other similar parcel of land essentially open to the outside air deeded, dedicated, or otherwise permanently appropriated to the public for public use and having a clear width and height of not less than 10 ft.
  The code intends a situation where occupants egressing from a building ultimately reach a point where they can move away from the building unimpeded and no longer need the protection of the Code.

## Slide 9: Egress Elements
EXIT ACCESS
EXIT
EXIT DISCHARGE
STREET
S
T
R
E
E
T
GROUND FLOOR

## Slide 20: Professional Requirements
PE Exam
  85 total questions
  11-17 questions on egress and occupant movement
  https://ncees.org/wp-content/uploads/PE-Fire-Oct-2020_CBT_with-standards.pdf
CSP Exam
  Part of Domain 4
SFPE core competencies

## Slide 21: Intent
Identify hazards
  No building is 100 % compliant
  Understand impact of deficiency
  Different than identifying code requirements

## Slide 22: Means of Egress
Identify minimum required widths
Determine the clear width
Explain the rules for the means of egress

## Slide 23: Historic Fire
Cocoanut Grove

## Slide 24: Means of Egress
Chapter 7 of NFPA101
  Chapter 10 of IBC
Fundamental to life safety

## Slide 25: Means of Egress Requirements
Level
  Not more than ¼ in
  More than ½ in change in level
Clearance
  7 ft 6 in
  6 ft 8 in
Slip resistant
No obstructions

## Slide 26: Decreasing Hazard
From corridor to a room
From one room to another room
Through kitchens
Through mechanical rooms
Rated enclosure to unprotected space
Enclosed stair to lobby
Stairs directly to outside

## Slide 27: Minimums
Doors and Corridors
Access: 36 in
Doors:
  Clear width
  28 in
  32 in
Cannot decrease in direction of travel
Stairs
44 in
  Exception 36 in
56 in
Cannot decrease in direction of travel

## Slide 28: Clear Width
Doors
Stairs
Corridors

## Slide 29: Landings
No decrease in width
Length equal to width of stairs
  48 in
At doors

## Slide 30: Exits
Calculate the number of exits required
Explain how the exit should not be used

## Slide 31: Historic Fire
Rhythm Nightclub

## Slide 32: Number of Exits
Based on the number of people
  Not dependent on type of occupancy
Assume single exit could be blocked
  50 %

## Slide 33: Horizontal Exit

## Slide 34: Exit Usage
Fire protection systems only

## Slide 35
Unit 7 35

## Slide 36: Maintenance of Exits

## Slide 37: Enclosures

## Slide 39: Doors and Corridors
Calculate the minimum size of doors and corridors
Identify the features of doors and corridors

## Slide 40: Historic Fire
Hartford Hospital

## Slide 41: Minimum Widths
NFPA rules
IBC rules

## Slide 42: Doors
Direction
Hardware
Locks
  Delays
Forces
Labels

## Slide 43: Doors
Automatic-closing
Self-closing
Level
  Width of leaf on either side
Egress side
Ingress side

## Slide 44: Revolving Doors
Typically not include in means of egress
Must have regular doors adjacent
Doors must break-away in direction of travel
Rules on speeds

## Slide 45: Doors
Single action
  No special knowledge
  No special tools
Lock side based on security

## Slide 46: Other Components
Identify other elements that can be part of the means of egress
Determine when other components are appropriate to use

## Slide 47: Historic Fire
Cook County Administration Building

## Slide 48: Others
Areas of Refuge
  Area to wait
    Separated
  Connected to means of egress
    48 in stair
  2 way communication
  Accessible
  Size
    A 30 in x 48 in wheelchair space per 200 occupants
Smoke Proof Enclosure
  Outside building
  Protected shaft

## Slide 49: Others
≥ 44 (30) in clear width
≤ 1 in 12 (8) slope
≤ 30 in (12 ft) rise per run
Landings
  Top and bottom
  Length ≥ 60 in if accessible, ≥ 48 in otherwise
Other provisions similar to stairs

## Slide 50: Others
Second means of egress
≤ 90 persons
100 % capacity independent
Training
  No general public
≥ 8 persons capacity
Lobby
  A 30 in x 48 in wheelchair space per 50 occupants
  3 ft2 for ≥ 50 % occupant load
Separated and two-way communication

## Slide 51: Others
Before Phase I
Stair replacement?
Shaft with stair
Signage
FFCP
  2 way communication
Building must have
  Voice alarm
  Sprinklers

## Slide 52: Others
60 persons capacity
≤ 25 % of capacity except in industrial
Must be allowed by occupancy chapter
  Not allowed for most
  Training required

## Slide 53: Others
Allowed in spaces with occupant loads < 4
  Unoccupied roofs
  Second option from storage elevators and boiler rooms
  Towers and elevated platforms around machinery
Dimensions
  17 in ≤ Clear width ≤ 24 in
  6 ft 8 in headroom
  50 ° ≤ Clear width ≤ 68 °
  Riser height ≤ 9.5 in
  Tread depth ≥ 9.5 in
    ≥ 5.67 in not overlapped
    Lateral separation ≤ 2 in

## Slide 54: Others

## Slide 55: Ladders
Access to unoccupied spaces
Second means of egress from storage elevators or boiler rooms with occupant loads < 4 persons
Towers and elevated platforms around machinery with occupant loads < 4 persons
> 75°
Lowest rung ≤ 12 in of surface

## Slide 56: Supplementary Escape Devices

## Slide 57: Stairs
Calculate the minimum size of stairs
Identify the features of stairs

## Slide 58: Historic Fire
Grenfell Tower

## Slide 59: Stairs are Simple
https://themindcircle.com/30-epic-stair-design-fails/

## Slide 60: Stair Widths
Exit lanes
  Not used by NFPA101 or IBC
Width calculations
  NFPA
  IBC

## Slide 61: Stairs
Size
Usage
Slip resistant
Marked
Changes in size
  3/16 in
  3/8 in

## Slide 62: Stair Terminology
Flight
Landing
Dog-leg
  Sinistral
  Dextral
Straight
Curved
Spiral

## Slide 63: Curved and Spiral Stairs

## Slide 64: Handrails and Guards
Shape
Location

## Slide 65: Outside Stairs
Account for fear of heights
  ≥ 36 ft
  Opaque ≥ 48 in
Separated from interior
Minimize water accumulation
≥ 50 % open on one side

## Slide 66: Occupant Loads
Select the appropriate number of people per exit
Determine the capacity of areas with merging flows

## Slide 67: Historic Fire
Dusseldorf Airport

## Slide 68: Assigning Exits

## Slide 69: Simultaneous Occupancy

## Slide 70: Evacuation Elevators
25 % population + 2 % wheelchairs

## Slide 71: Merging Flows
Corridors
Stairs

## Slide 72: Balconies and Mezzanines

## Slide 73: Occupant Loads
Select the appropriate choice between gross and net area
Calculate the occupant load

## Slide 74: Historic Fire
Ghost Ship

## Slide 75: Occupant Load Factors
Gross
Net
Mixed use

## Slide 76: Occupant Load Factors
Minimum design value
  Are more people acceptable?
Origin of load factors
Meaning of words
  Based on use
Rounding rules

## Slide 77: Seating Arrangements
Concentrated
Less concentrated
Fixed
Bench
Waiting spaces

## Slide 78: Malls
Load factor varies with size of mall

## Slide 79: Exits
Determine the remoteness of exits
Calculate the capacity of exits

## Slide 80: Historic Fire
Katie Jane Memorial Home

## Slide 81: Remote
Rules for two exits
  Additional exits as far apart as is practical
Sprinkler trade-off
No familiarity requirements

## Slide 82: Requirements
Openings from normally occupied spaces
Rating depends on building height
  1 hr for 3 stories or less
  2 hr for 4 stories or more

## Slide 83: Discharge
Remote
All outside
  50 % in some instances
Barrier

## Slide 84: Capacity
Typically for existing buildings
  Change of use
  Reconstruction on floor
Look for limiting component
  More to consider than just the first component
Rounding

## Slide 85: Distances
Determine where distance calculations are required
Calculate distances
Explain the limits on dead end corridors and common path of travel

## Slide 86: Historic Fire
Iroquois Theater

## Slide 87: Travel Distance
When to measure
Two paths
EXIT ACCESS
EXIT
EXIT DISCHARGE
STREET
S
T
R
E
E
T
GROUND FLOOR

## Slide 88: Rooms
How to measure

## Slide 89: Corridors
Natural path
Minimum 12 in clearance around curves/obstructions
To exit
  Door

## Slide 90: Stairs
On treads
On landing

## Slide 91: Areas of Concern
Dead End Corridors
Common Path of Travel