## Slide 1: ASET
Predict time to incapacitation
Calculate the available egress time

## Slide 2: Historic Fire
DuPont Plaza Hotel

## Slide 3: ASET
Meaning of acronym
Times included

## Slide 4: Fire Growth
t2
  Based on reaching 1000 Btu/s (1055 kW)
    Slow: 0.28*10-2 Btu/s3, t=600s
    Medium: 1.11*10-2 Btu/s3, t=300s
    Fast: 4.44*10-2 Btu/s3, t=150 s
    Ultrafast: 17.78*10-2 Btu/s3, t=75 s
Notes: 4

## Slide 5
Smoke Plume
Where:
Tp=Smoke plume temperature
    c=Convective heat release rate
    =Mass entrainment rate
Cp=Specific heat
T0=Ambient temperature
Notes: 5

## Slide 6
Smoke Plume
Where:
    =Volumetric flow rate (m3/s)
Tp=Smoke plume temperature (°C)
    =Mass entrainment rate (kg/sec)
Notes: 6

## Slide 7: Smoke Production
  Where:
  = Mass flow in plume at height z (kg/s)
  k= Wall factor
  c= Convective heat release rate of fire (kW)
  z= Height above top of fuel (m)

## Slide 8
Ceiling Jet
Where:
r/H>0.18
ΔT=Temperature change (°C)
=Total heat release rate (kW)
H=Height (m)
r=Distance from center of plume (m)
Notes: 8

## Slide 9
Ceiling Jet
  Where:
  r/H>0.15
Ucj=Velocity (m/s)
=Total heat release rate (kW)
H=Height (m)
r=Distance from center of plume (m)
Notes: 9

## Slide 10
Activation Times
Where:
Td=Temperature of detector (°C)
Ucj=Velocity (m/s)
Tcj=Temperature of ceiling jet (°C)
RTI= Response Time Index (m0.5*s0.5)
Δt= Time step (s)
Notes: 10

## Slide 11
Smoke
    Where:
    CO=concentration (ppm)
    RMV=breathing rate (L/min)
    Where:
    Ci=Concentration at given time
    Cti=Dose at endpoint
Notes: 11

## Slide 12
Tenability
FIN=((FICO+FICN+FLCirr)*VCO2+FEDIO)
See 3-130 or 6-18 in NFPA Handbook for details
Irritants can cause incapacitation
  See FEC equation (6-24)
Notes: 12

## Slide 13
Visibility
Incapacitation when not able to see exits
  2 ft (0.6 m) cannot see own hand
  16.4 ft (5 m) visibility where familiar
  49 ft (15 m) visibility where unfamiliar
Where:
Vis=Visibility distance (m)
K=Constant
D=Optical density (m-1)
Notes: 13

## Slide 14
Heat
Skin burns
  Skin temperature 113 °F (44.8 °C)
  2.5 kW/m2
  392 °F (200 °C)
Respiratory burns
  140 °F (60 °C)
Hyperthermia
  248 °F (121 °C)
  150 °F (66 °C)
Notes: 14

## Slide 15
Heat
  Where:
    tI,rad=Time to incapacitation from radiation (min)
    r=Radiant heat exposure dose at endpoint (1.33 for pain, 10 for incapacitation from serious injury)
=Heat flux (kW/m2)
Where:
tI,conv=Time to incapacitation from convection (min)
T=Temperature at skin surface (°C)
Notes: 15