## Slide 1: International Building Code
Apply the rules for height and areas of buildings
Perform calculations related to adjustment factors

## Slide 2: Historic Fire
MGM Grand

## Slide 3: Height and Area
Sections 504 and 506
  Sprinklers generally increase by 20 ft and 1 story for height
  Sprinklers add 2 or 3 times original area

## Slide 4: Modifications of Area Limits
Aa=At+[At*If]+[At*Is]
or
Aa=At+[NS*If]
Where:
Aa= Allowable area per floor
At= Allowable area from Table
If= Area factor increase due to frontage
Is= Area factor increase due to sprinklers

## Slide 5: Area factor for sprinklers
Is=3 for buildings one story above ground
Is=2 for buildings more than one story above ground

## Slide 6: Area Factor for Frontage
Where:
  If= Area factor increase due to frontage
  F= Building perimeter with frontage (ft)
  P= Total building perimeter (ft)
  W= Width of the frontage (ft)
Note: W/30 not permitted to exceed 1.0
W must be at least 20 ft

## Slide 7: Area Factor for Frontage
% of Perimeter | Open Space <20 ft | Open Space 20 to <25 ft | Open Space 25 to <30 ft | Open Space 30 ft or more
<25 | 0 | 0 | 0 | 0
25 to <50 | 0 | 0.17 | 0.21 | 0.25
50 to <75 | 0 | 0.33 | 0.42 | 0.50
75 or greater | 0 | 0.50 | 0.63 | 0.75
New table values in 2021
New values are at the lower end of each range
Interpolation allowed
  Client will want you to use linear interpolation
  Old equation was linear interpolation
  All values are still the same

## Slide 8: Example 1
What are the height and area limitations for a Group M occupancy in a building of Type III B construction?
Solution: 2 Stories, 12,500 ft2 per floor.

## Slide 9: Example 2
What are the height and area limitations for a library in an unprotected steel building without sprinklers?
Solution: 2 Stories, 9,500 ft2 per floor

## Slide 10: Example 3
Are the height and area of the building acceptable?
  Building is unsprinklered
  Frontage on two adjacent sides 25 feet wide
  2 Stories
  110 ft x 100 ft
  Type V-B Construction
  Group B occupancy

## Slide 11: Example 3
Need 11,000 ft2, 2 stories
9,000 ft2, 2 stories
Allowance for frontage:
Total area allowed:
  Aa=9,000+[9,000*0.208]+[9,000*0]=10,875 ft2

## Slide 12: Example 3
Options
  Just tell the owner no
  Ask the owner to make their building smaller
  Relocate building on site to increase frontage
  Change to different construction type
    Protect structural elements
    Change material
  Add sprinklers

## Slide 13: Example 4
Are the area and height acceptable if frontage 30 ft wide exists on all sides?
  Sprinklered
  3 Stories
  130 ft x 360 ft
  Group E Occupancy
  Type II B Construction

## Slide 14: Example 4
Need 46,800 ft2, 3 stories
Nonsprinklered: 14,500 ft2, 2 stories
Sprinklers can increase to 3 stories
Allowance for frontage:
Total area allowed:
  Aa=14,500+[14,500*0.75]+[14,500*2]=54,375 ft2
  =43,500+[14,500*0.75]=54,375 ft2

## Slide 15
Street 60 Feet Wide
60 ‘ Street
Using the information given, determine if the building may be of Type V-B Construction as proposed

## Slide 16: Example 5
Group B Occupancy, Type V-B: 9000 ft2
Varying frontage = check multiple configurations
  Option 1: 20 ft frontage on all sides
  Option 2: 30 ft frontage on 83%
  Use Option 2
Total area allowed:
  Aa=9,000+[9,000*0.579]+[9,000*0]=14,211 ft2