## Slide 1: Scenarios
Explain the PBD process
Select appropriate evacuation scenarios
Identify appropriate fire scenarios

## Slide 2: Historic Fire
Beverly Hills Supper Club

## Slide 3: Performance Based Option
Chapter 5 of NFPA101
No rules
  Goals and objectives
  Some prescriptive rules stay
All stakeholders
  Assumptions
  Agreement
Establish performance criteria

## Slide 4: Safety Assessment
<
Safe
Available Safe Escape Time (ASET)
Required Safe Escape Time (RSET)

## Slide 5: Occupant Scenarios
Characteristics
  Physical
  Cognitive
Number
  High density
  Low density
Location
Activities
  Actions
  Decisions
Trained staff
Building life cycle
Off-site conditions

## Slide 6: Prescribed Occupant Scenarios

## Slide 7: Potential Occupant Scenarios: Characteristics
Sensibility
Reactivity
Mobility
Susceptibility
Normal conditions
Elderly
Children
Disabled

## Slide 8: Potential Occupant Scenarios: Number and Location
Normal conditions
Maximum occupant load
  All occupied rooms
  Average density
  Special occasion
Low occupant load

## Slide 9: Potential Occupant Scenarios: Activities and Staff
Normal conditions
Delays
  Role
  Familiarity
  Actions
  Decisions
Staff assistance
Emergency response personnel

## Slide 10: Potential Occupant Scenarios Building and Off-Site Conditions
Post-construction
Off-site

## Slide 11: Fire Scenario Considerations
Identify the specific fire safety challenges
Location of the fire
Type of fire
Potential complicating hazards leading to other fire scenarios
Systems and features impacting the fire
Occupant actions impacting the fire

## Slide 12: Prescribed Fire Scenarios
Occupancy specific typical fire
Ultrafast fire in primary means of egress

## Slide 13: Prescribed Fire Scenarios
Starts in normally unoccupied room with large number of people in another area
Concealed space fire adjacent to a large room

## Slide 14: Prescribed Fire Scenarios
Slow fire shielded from systems near high occupancy
Severe fire characteristic of the building

## Slide 15: Prescribed Fire Scenarios
Outside exposure fire
Ordinary combustibles fire without passive fire protection system functioning
Ordinary combustibles fire without active fire protection system functioning

## Slide 16: Scenario Selection
Must address all potential scenarios
  Realistic
  Do not have to model all
Results must be documented

## Slide 17: Analysis
Deterministic vs. Probabilistic
Sensitivity analysis