## Slide 1: Methodologies
Explain how means of egress rules have been developed
Identify other methods of determining people movement
Explain the limitations of existing methodologies

## Slide 2: Historic Fire
Daegu Subway

## Slide 3: Origins of Egress Requirements
Stair width
  First building code (1905): 20 in
  NFPA committee (1913): 44 in, handrails protrude 3.5 in
    Based on people standing in stair (28 per floor)
    22 in per person on every other tread (from soldiers standing in line)
    “Sufficient” to prevent three people from forming arch and blocking traffic
  Why stairs are based on single floor at a time

## Slide 4: Flow Method
Based on number of people per minute per exit lane
  Level 60 persons/min
  Stairs 45 persons/min
  Stairs later found to be closer to 27 persons/min
Still used in NFPA 130
Time based
  4 min for platform
  6 min to point of safety
Level
  2.08 persons/in-min
  124 ft/min
Stairs
  1.41 persons/in-min
  48 ft/min (vertical)

## Slide 5: Level of Service
Concept from transportation
  Pathfinder allows you to view
Ability of people to freely choose their own speed
  A: Free to choose own speed and pass
  B: Free to choose own speed and pass, minor conflicts
  C: Speed and passing restricted, major conflicts
  D: Cannot pass
  E: Intermittent stoppages
  F: Movement to shuffle, not suited for design

## Slide 6: Level of Service

## Slide 7: Behavior

## Slide 8: Behavior

## Slide 9: Behavior
Stairs
  Preference