## Slide 1: RSET
Calculate the required safe egress time

## Slide 2: Historic Fire
Shanghai Apartment

## Slide 3: Time
Detection and notification
Reaction
Pre-evacuation
Travel time

## Slide 4: Effective Width
Boundary layer

## Slide 5: Movement Times
SFPE equation
  Pauls, Fruin, Predtechenskii and Milinskii
  Beyond data collected
  Not internally consistent
  Age of data
  Diversity of population
  Distribution
  No data to support k
Notes: 5

## Slide 6: Observed Flows

## Slide 7: Movement Times
Where:
S=speed (ft/min or m/s)
k=constant (Table 4.2.5)
a=constant (2.86 when using ft, 0.266 when using m)
D=density (persons/ft2 or persons/m2)
Notes: 7

## Slide 8: Justification of k-Factors
Element | k (U.S. units) | k (metric)
Corridor, door, ramp | 275 | 1.40
Stairs |  | 
Riser, Tread (in) |  | 
7.5, 10 | 196 | 1.00
7.0, 11 | 212 | 1.08
6.5, 12 | 229 | 1.16
6.5, 13 | 242 | 1.23

## Slide 9: Movement Times
  Where:
  Fs= Specific flow (persons/ft-min or persons/m-s)
  We=Effective width (ft or m)
  in,out= arriving at, after
Element | Boundary Layer (in)
Stairways | 6
Railing, handrails | 3.5
Theater chairs | 0
Corridor, ramp | 8
Obstacles | 4
Wide concourses | < 18
Door | 6
Notes: 9

## Slide 10: Movement Times
Calculations build
  See example problem on 4-62 to 4-64 in NFPA Handbook
Consider limiting component
Notes: 10

## Slide 11: Movement Times
Speed in reduced visibility
Where:
W= movement speed (m/s)
aK= Extinction coefficient (m-1)
Notes: 11

## Slide 12: Flow

## Slide 13: Population Variability
Age
Fitness
Gender
Fatigue